PR COOLING LTD

FACTORY-SPECIFIC EMERGENCY RESPONSE PLAN

Refrigerant Leak – Industrial Refrigeration Systems

Project: 
Site: Factory Environment
Date: 
Prepared By: PR Cooling Ltd

1. PURPOSE OF THIS PLAN

To provide clear, immediate actions for engineers, factory staff, and supervisors in the event of a refrigerant leak during installation, servicing, or commissioning of refrigeration equipment within a factory environment.

This plan covers leaks involving:

- A1 refrigerants: R404A, R452A, R134a

- A2L refrigerants: R32

- A3 refrigerants: R290 (Propane)

- Natural refrigerants: CO₂ (R744)

2. GENERAL PRINCIPLES

- Do not attempt to stop a leak without proper PPE and training

- Never enter a confined or poorly ventilated area where refrigerant may have accumulated

- Evacuate immediately if flammable refrigerants are involved

- Prioritise life safety over equipment protection

3. IMMEDIATE ACTIONS (ALL REFRIGERANTS)

3.1 Stop Work Immediately

- Cease all installation, brazing, electrical, or commissioning activities

- Shut down tools and equipment

3.2 Raise the Alarm

- Notify factory supervisor

- Inform all personnel in the vicinity

- Use radios or hand signals if noise levels are high

3.3 Evacuate the Area

- Move upwind of the leak

- Avoid low-lying areas (refrigerants can pool)

- Do not re-enter until authorised

3.4 Ventilate

- Open doors, roller shutters, and windows

- Activate extraction fans if safe to do so

- Do not operate electrical switches if flammable refrigerants are involved

4. REFRIGERANT-SPECIFIC RESPONSE ACTIONS

4.1 A1 Refrigerants (R404A, R452A, R134a)

Hazards: Asphyxiation, frostbite

Actions

- Ventilate area

- Evacuate personnel

- Use portable gas detector if available

- Only trained F-Gas engineers may isolate leak

- Avoid confined spaces

4.2 A2L Refrigerants (R32)

Hazards: Mild flammability, asphyxiation

Actions

- Stop all hot work

- Eliminate ignition sources

- Ventilate area

- Evacuate personnel

- Use intrinsically safe leak detectors

- Only trained personnel to isolate leak

4.3 A3 Refrigerants (R290 – Propane)

Hazards: Highly flammable, explosion risk

Actions

- Evacuate immediately

- Do NOT operate electrical switches

- Do NOT use mobile phones

- Eliminate ignition sources

- Ventilate naturally (doors, shutters)

- Call fire service if ignition risk is present

- Only hydrocarbon-trained engineers may isolate leak

4.4 CO₂ (R744)

Hazards: High pressure, asphyxiation, cold burns

Actions

- Evacuate area

- Ventilate

- Do not approach leaking high-pressure lines

- Monitor oxygen levels if equipment available

- Only trained CO₂ engineers to isolate leak

5. FIRST AID MEASURES

Inhalation

- Move casualty to fresh air

- Keep warm and at rest

- Call emergency services if breathing is difficult

Skin Contact (Frostbite)

- Warm affected area with lukewarm water

- Do not rub skin

- Seek medical attention

Eye Contact

- Rinse with clean water for at least 15 minutes

- Seek medical attention

6. FACTORY-SPECIFIC CONTROLS

6.1 Machinery Shutdown

- Stop nearby machinery if refrigerant could be drawn into intakes

- Prevent refrigerant from entering production lines

6.2 Evacuation Routes

- Use factory-designated escape routes

- Avoid low-lying corridors or pits

6.3 Communication

- Use radios or hand signals in high-noise areas

- Notify control room or site manager immediately

7. ISOLATION & CONTAINMENT

Only trained PR Cooling Ltd engineers may:

- Close service valves

- Recover refrigerant

- Repair leaks

- Restart equipment

Do NOT:

- Attempt to repair leaks without PPE

- Use unapproved leak-sealing products

- Re-enter area until gas levels are confirmed safe

8. REPORTING REQUIREMENTS

- Complete incident report

- Notify F-Gas register if required

- Record refrigerant loss

- Update site logbook

- Review RAMS and update if necessary

9. AUTHORISATION

Prepared By: __________________________
Approved By: __________________________
Date: _________________________________