Location Address:

Number of Installers:

Method Statement Date:Click or tap to enter a date.

Method Statement – Repairs to Chiller Units

1. Scope of Works

This method statement covers the safe system of work for carrying out repairs, servicing, diagnostics, and component replacement on commercial/industrial chiller units. Tasks may include electrical testing, refrigerant handling, mechanical repairs, leak detection, and functional commissioning.

2. Responsibilities

- PR Cooling Ltd Engineer: Carry out works in accordance with RAMS, site rules, and manufacturer guidance.

- Site Representative: Provide access, isolation permissions, and relevant site information.

- Supervisor/Manager: Ensure engineers are competent, equipped, and briefed.

3. Required Competence

- F-Gas certified engineer

- Electrical competence (18th Edition or equivalent)

- Manufacturer-specific training where applicable

- Awareness of site safety procedures and emergency arrangements

4. Tools & Equipment

- Standard HVAC tool kit

- Electrical testing equipment (multimeter, clamp meter)

- Refrigerant recovery machine & cylinders

- Vacuum pump

- Leak detection equipment

- Lifting aids (where required)

- PPE as specified in the risk assessment

5. PPE Requirements

- Safety boots

- Hi-vis clothing

- Safety glasses/goggles

- Gloves (mechanical and thermal)

- Hearing protection (as required)

- Respiratory protection if required by COSHH

6. Method of Work

6.1 Arrival & Preparation

- Report to site reception and complete sign-in procedures.

- Attend site induction if required.

- Review RAMS and carry out a dynamic risk assessment.

- Confirm work area is safe, accessible, and adequately lit.

- Establish exclusion zone around chiller if in public or shared areas.

6.2 Isolation Procedures

- Liaise with site representative to isolate electrical supplies.

- Apply lock-off and tag-out devices.

- Verify dead using approved testing equipment.

- Isolate pumps, fans, and associated mechanical systems.

- Confirm refrigerant pressures have stabilised before opening circuits.

6.3 Accessing the Chiller Unit

- Remove panels using appropriate tools.

- Store panels safely to avoid trip hazards or damage.

- Ensure no unauthorised persons enter the work area.

6.4 Diagnostic Checks

- Conduct visual inspection for leaks, damage, or electrical faults.

- Use approved leak detection methods (electronic, nitrogen pressure test, etc.).

- Perform electrical tests as required (continuity, resistance, voltage).

- Identify faulty components and confirm repair plan.

6.5 Refrigerant Handling (if required)

- Connect recovery machine and approved recovery cylinder.

- Recover refrigerant in accordance with F-Gas regulations.

- Label cylinders clearly and store upright.

- Ensure adequate ventilation throughout.

- Avoid hot works near refrigerant lines containing flammable gases (e.g., R32).

6.6 Mechanical Repairs

- Remove faulty components using correct tools and lifting aids.

- Replace with manufacturer-approved parts.

- Ensure all pipework joints are clean and prepared before brazing (if applicable).

- Pressure-test repaired sections using nitrogen to manufacturer specifications.

- Evacuate system to required micron level using vacuum pump.

6.7 Recharging System

- Charge system with correct refrigerant type and quantity.

- Monitor subcooling, superheat, and operating pressures.

- Check for leaks after charging.

6.8 Electrical Repairs

- Replace faulty electrical components (contactors, sensors, boards, etc.).

- Ensure all wiring is correctly terminated and secured.

- Reinstate panel covers before energising.

6.9 Recommissioning

- Remove lock-off devices and re-energise system.

- Run chiller through full operating cycle.

- Check:

  - Compressor operation

  - Fan speeds

  - Flow rates

  - Temperature differentials

  - Alarms and safety devices

- Adjust settings as required.

6.10 Completion of Works

- Replace all panels and ensure unit is left in safe condition.

- Remove tools, waste, and materials from site.

- Dispose of refrigerant and waste in accordance with environmental regulations.

- Complete service/repair report and obtain client sign-off.

7. Environmental Considerations

- Prevent refrigerant release to atmosphere.

- Use drip trays to contain oil.

- Dispose of waste materials responsibly.

- Avoid noise disturbance where possible.

8. Emergency Procedures

- Follow site emergency arrangements.

- In case of refrigerant leak: evacuate area, ventilate, and notify site management.

- For electrical incidents: isolate supply and seek medical assistance.

- Fire: raise alarm and use appropriate extinguisher (CO₂/dry powder).

This method statement will be reviewed annually or at any time, where a significant change requires a review.

Signed by: Rob Chappell		Signature:

Health & Safety Consultant		Dated: 28/03/2026	Next Review: 12 Months